## InputOverview
Name | Address | RegCount | Description
Device | 0 | 6 | Protocol and controller setup
DiscreteIO | 100 | 17 | Input / output bits (on/off)
AnalogIO | 200 | 23 | Input / output words
Time | 300 |  | Clock and calendar
Alarm | 400 | 10 | Alarm and message handling
WeekProgram | 500 |  | Calendar based programming
UserFunctions | 600 |  | User input function selection
DataLog | 700 |  | Data, alarm and event logging
Control | 1000 | 4 | System control and status
AirFlow | 1100 | 5 | Ventilation control
AirTemp | 1200 | 7 | Room temperature control
AirBypass | 1300 |  | Exchanger bypass control
AirHeat | 1400 |  | Inlet air heater control
Compressor | 1500 | 1 | Compressor operation control
Defrost | 1600 |  | Defrosting control
HotWater | 1700 | 2 | Hot water control
CentHeat | 1800 | 1 | Central heating control (EK)
AirQual | 1900 |  | Air quality control (RH, CO2)
UserPanel | 2000 |  | Display and keyboard
PreHeat | 2100 | 1 | Intake air preheat / earth tube
DPT | 2200 | 3 | Difference pressure transducer
Display | 3000 | 10 | Display information
Alarm | 3050 | 26 | Alarm log
AirQuality | 3100 | 3 | Air quality display

## InputRegisters
id | Address | Scale | units | title | ID
Bus.Version | 0 |  |  | Protocol version number | speaker_playing
App.VersionMajor | 1 | text |  | Software version - major (2 character ascii text)
App.VersionMinor | 2 | text |  | Software version - minor (2 character ascii text)
App.VersionRelease | 3 | text |  | Software version - release (2 character ascii text)
Info.AppID | 4 |  |  | Application Id
Info.HWType | 5 |  |  | Application hardware Id
Input.UserFunc | 100 |  |  | User function
Input.AirFilter | 101 |  |  | Air filter alarm | onoff
Input.DoorOpen | 102 |  |  | Door contact | onoff
Input.Smoke | 103 |  |  | Smoke alarm | alarm_smoke
Input.MotorThermo | 104 |  |  | Motor thermo fuse | onoff
Input.Frost_Overht | 105 |  |  | Heating surface frost / overheat | onoff
Input.AirFlow | 106 |  |  | Airflow monitor | onoff
Input.P_HI | 107 |  |  | High pressure switch | onoff
Input.P_LO | 108 |  |  | Low pressure switch | onoff
Input.Boil | 109 |  |  | Hot water boiling
Input.3WayPos | 110 |  |  | Hot water 3-way valve position | onoff
Input.DefrostHG | 111 |  |  | Hotgas defrost type selection | onoff
Input.Defrost | 112 |  |  | Defrost thermostat | onoff
Input.UserFunc_2 | 113 |  |  | User function 2
Input.DamperClosed | 114 |  |  | Air damper closed position switch | onoff
Input.DamperOpened | 115 |  |  | Air damper opened position switch | onoff
Input.FCorThermoAl | 116 |  |  | Combined FC and thermo alarm | onoff
Input.T0_Controller | 200 | 100 | °C | Controller board temperature | measure_temperature
Input.T1_Intake | 201 | 100 | °C | Fresh air intake temperature | measure_temperature
Input.T2_Inlet | 202 | 100 | °C | Inlet temperature (before heater) | measure_temperature
Input.T3_Exhaust | 203 | 100 | °C | Room exhaust temperature | measure_temperature
Input.T4_Outlet | 204 | 100 | °C | Outlet temperature | measure_temperature
Input.T5_Cond | 205 | 100 | °C | Condenser temperature | measure_temperature
Input.T6_Evap | 206 | 100 | °C | Evaporator temperature | measure_temperature
Input.T7_Inlet | 207 | 100 | °C | Inlet temperature (after heater) | measure_temperature
Input.T8_Outdoor | 208 | 100 | °C | Outdoor temperature | measure_temperature
Input.T9_Heater | 209 | 100 | °C | Heating surface temperature | measure_temperature
Input.T10_Extern | 210 | 100 | °C | External room temperature | measure_temperature
Input.T11_Top | 211 | 100 | °C | Hot water top temperature | measure_temperature
Input.T12_Bottom | 212 | 100 | °C | Hot water bottom temperature | measure_temperature
Input.T13_Return | 213 | 100 | °C | EK return temperature | measure_temperature
Input.T14_Supply | 214 | 100 | °C | EK supply temperature | measure_temperature
Input.T15_Room | 215 | 100 | °C | User panel room temperature | measure_temperature
Input.T16 | 216 | 100 | °C | AUX temperature (Hotwater anode) | measure_temperature
Input.T17_PreHeat | 217 | 100 | °C | Preheater or earth tube air intake temperature | measure_temperature
Input.T18_PresPibe | 218 | 100 | °C | Pressure pibe temperature | measure_temperature
Input.pSuc | 219 |  | bar | Suction pressure | measure_pressure
Input.pDis | 220 |  | bar | Dischage pressure | measure_pressure
AirQual.RH | 221 | 100 | % | Humidity sensor value | measure_humidity
AirQual.CO2 | 222 |  | ppm | Carbon dioxide sensor value
Alarm.Status | 400 |  |  | Alarm state bit mask
Alarm.List_1_ID | 401 |  |  | Alarm 1 - Code
Alarm.List_1_Date | 402 |  |  | Alarm 1 - Date
Alarm.List_1_Time | 403 |  |  | Alarm 1 - Time
Alarm.List_2_ID | 404 |  |  | Alarm 2 - Code
Alarm.List_2_Date | 405 |  |  | Alarm 2 - Date
Alarm.List_2_Time | 406 |  |  | Alarm 2 - Time
Alarm.List_3_ID | 407 |  |  | Alarm 3 - Code
Alarm.List_3_Date | 408 |  |  | Alarm 3 - Date
Alarm.List_3_Time | 409 |  |  | Alarm 3 - Time
Control.RunAct | 1000 |  |  | Actual on/off state
Control.ModeAct | 1001 |  |  | Actual operation mode
Control.StateDisplay | 1002 |  |  | Actual control state
Control.SecInState | 1003 |  | Sec | Actual time in state
AirFlow.VentSet | 1100 |  | Step | Actual ventilation step set point 0 : Off
AirFlow.InletAct | 1101 |  | Step | Actual inlet fan speed step 0 : Off
AirFlow.ExhaustAct | 1102 |  | Step | Actual exhaust fan speed step 0 : Off
AirFlow.SinceFiltDay | 1103 |  | Days | Days since last air filter change alarm
AirFlow.ToFiltDay | 1104 |  | Days | Days to next air filter change alarm
AirTemp.IsSummer | 1200 |  |  | Summer state
AirTemp.TempInletSet | 1201 | 100 | °C | Inlet temperature request (T7 setpoint)
AirTemp.TempControl | 1202 | 100 | °C | Actual value for controlled temperature
AirTemp.TempRoom | 1203 | 100 | °C | Actual room temperature (T15 or T10)
AirTemp.EffPct | 1204 | 100 | % | Passive heat exchanger efficiency calculation
AirTemp.CapSet | 1205 | 100 | % | Requested capacity
AirTemp.CapAct | 1206 | 100 | % | Actual capacity
Compressor.Type | 1500 |  | 0..2 | 0: None, 1: On/Off, 2: Modulated hotgas valve
HotWater.Type | 1700 |  | 0..3 | 0: None, 1:Only hotware (VGU), 2:With ventilation (VP), 3:With central heating (VGU180) | thermostat_mode
HotWater.AnodeState | 1701 |  | 0..3 | 0=OFF, 1=OK, 2=SERVICE, 3=ERROR | thermostat_mode
CentralHeat.HeatExtSet | 1800 | 100 | °C | Actual setpoint for external heating source | target_temperature
PreHeat.BlockRemain | 2100 |  | Sec | Remaining time for the pre-heater blocking function commanded by the HR 2100 register
DPT.InSession | 2200 | 0.1 |  | 1 if DPT node is in session
DPT.AirFlow1 | 2201 |  | m3/h | Calculated air flow 1
DPT.AirFlow2 | 2202 |  | m3/h | Calculated air flow 2
AirBypass.IsOpen | 3000 |  |  | Bypass damper 0: Closed
Output.AirHeatCap | 3001 | 100 | % | After heating element
Defrost.ExchDefrost | 3002 |  |  | De-icing heat exchanger 0: Off
AirQual.CO2_Enable | 3003 |  |  | CO2 sensor present in the system or not 0: Off | button
AirFlow.RoomReduce | 3004 |  |  | Stop at low room temperature 0-4
AirFlow.LastTestDay | 3005 |  |  | Date for last air damper self-test
AirFlow.SinceFiltDay | 3006 |  |  | Days since last air filter change
AirFLow.WinterReduce | 3007 |  |  | Low fan speed at low outdoor temperature Level 0-4
AirTemp.TempSet | 3008 | 100 | °C | Actual resulting set-point for room temperature 5.00°C - 50.00°C
AirTemp.TempControl | 3009 | 100 | °C | Master sensor for the controlled temperature (room / inlet) | measure_temperature
Alarm.LogEventID | 3050 |  |  | Event log ID (alarm code) 0 – 255
Alarm.LogDate | 3051 | DATE_DOS |  | Date of actual indexed event log
Alarm.LogTime | 3052 | TIME_DOS |  | Time of actual indexed event log
Alarm.LogT1 | 3053 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT3 | 3054 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT4 | 3055 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT5 | 3056 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT6 | 3057 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT7 | 3058 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT8 | 3059 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT9 | 3060 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT10 | 3061 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT11 | 3062 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT12 | 3063 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT13 | 3064 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT14 | 3065 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT15 | 3066 |  | °C | Log item temperatures | measure_temperature
Alarm.LogDI_1_8i | 3067 |  |  | Log item digital input 1-8: bit 0 = input 1
Alarm.LogDI_9_16 | 3068 |  |  | Log item digital input 9-16: bit 0 = input 9
Alarm.LogDO_1_8 | 3069 |  |  | Log item digital output 1-8: bit 0 = output 1
Alarm.LogDO_9_16 | 3070 |  |  | Log item digital output 9-16: bit 0 = output 9
Alarm.LogAO_1 | 3071 |  | % | Log item analoge output 1 0 - 100
Alarm.LogAO_2 | 3072 |  | % | Log item analoge output 2
Alarm.LogAO_3 | 3073 |  | % | Log item analoge output 3 0 – 100
Alarm.LogAO_4 | 3074 |  | % | Log item analoge output 4 0 - 100
Alarm.LogCtrState | 3075 |  |  | Operation states for Control module 0: OFF
AirQual.RH_Avg | 3100 | 100 | % | Humidity average value. Range: 0..100.00 | measure_humidity
Opt9_1.BoardId | 3101 |  |  | If expansion I/O board is present the value must be 12.
AirFlow.VentState | 3102 |  |  | Ventilation state 0: OFF | thermostat_mode

## HoldingRegisters
Name | type | address | scale | units | title | desc | Min | Max | capability | uiComponent | values | getable | setable | insights | icon
Bus.Address | boolean | 50 |  |  | Protocol node address (default = 30) | Protocol node address (default = 30) | 0 | 255 | onoff | toggle |  | true | true
Output.AirFlap | boolean | 100 |  |  | Air flap | Air flap |  |  | onoff | toggle |  | true | true
Output.SmokeFlap | boolean | 101 |  |  | Smoke flap | Smoke flap |  |  | onoff | toggle |  | true | true
Output.BypassOpen | boolean | 102 |  |  | Bypass flap open | Bypass flap open |  |  | onoff | toggle |  | true | true
Output.BypassClose | boolean | 103 |  |  | Bypass flap close | Bypass flap close |  |  | onoff | toggle |  | true | true
Output.AirCircPump | boolean | 104 |  |  | Air heat circulation pump | Air heat circulation pump |  |  | onoff | toggle |  | true | true
Output.AirHeatAllow | boolean | 105 |  |  | Air heating selected | Air heating selected |  |  | onoff | toggle |  | true | true
Output.AirHeat_1 | boolean | 106 |  |  | Air heater relay 1 | Air heater relay 1 |  |  | onoff | toggle |  | true | true
Output.AirHeat_2 | boolean | 107 |  |  | Air heater relay 2 | Air heater relay 2 |  |  | onoff | toggle |  | true | true
Output.AirHeat_3 | boolean | 108 |  |  | Air heater relay 3 | Air heater relay 3 |  |  | onoff | toggle |  | true | true
Output.Compressor | boolean | 109 |  |  | Compressor | Compressor |  |  | onoff | toggle |  | true | true
Output.Compressor_2 | boolean | 110 |  |  | Compressor 2 | Compressor 2 |  |  | onoff | toggle |  | true | true
Output.4WayCool | boolean | 111 |  |  | 4-way valve | 4-way valve |  |  | onoff | toggle |  | true | true
Output.HotgasHeat | boolean | 112 |  |  | Hotgas valve - heat | Hotgas valve - heat |  |  | onoff | toggle |  | true | true
Output.HotgasCool | boolean | 113 |  |  | Hotgas valve - cool | Hotgas valve - cool |  |  | onoff | toggle |  | true | true
Output.CondOpen | boolean | 114 |  |  | Air condenser active | Air condenser active |  |  | onoff | toggle |  | true | true
Output.CondClose | boolean | 115 |  |  | Air condenser inactive | Air condenser inactive |  |  | onoff | toggle |  | true | true
Output.WaterHeat | boolean | 116 |  |  | Hot water heater | Hot water heater |  |  | onoff | toggle |  | true | true
Output.3WayValve | boolean | 117 |  |  | Hot water 3-way valve | Hot water 3-way valve |  |  | onoff | toggle |  | true | true
Output.CenCircPump | boolean | 118 |  |  | EK circulation pump | EK circulation pump |  |  | onoff | toggle |  | true | true
Output.CenHeat_1 | boolean | 119 |  |  | EK heater relays 1 | EK heater relays 1 |  |  | onoff | toggle |  | true | true
Output.CenHeat_2 | boolean | 120 |  |  | EK heater relays 2 | EK heater relays 2 |  |  | onoff | toggle |  | true | true
Output.CenHeat_3 | boolean | 121 |  |  | EK heater relays 3 | EK heater relays 3 |  |  | onoff | toggle |  | true | true
Output.CenHeatExt | boolean | 122 |  |  | External radiator heat | External radiator heat |  |  | onoff | toggle |  | true | true
Output.UserFunc | boolean | 123 |  |  | User function active | User function active |  |  | onoff | toggle |  | true | true
Output.UserFunc_2 | boolean | 124 |  |  | User function active 2 | User function active 2 |  |  | onoff | toggle |  | true | true
Output.Defrosting | boolean | 125 |  |  | Defrost function active | Defrost function active |  |  | onoff | toggle |  | true | true
Output.AlarmRelay | boolean | 126 |  |  | Alarm relay state | Alarm relay state |  |  | onoff | toggle |  | true | true
Output.PreHeat | boolean | 127 |  |  | Preheater or earth tube activation | Preheater or earth tube activation |  |  | onoff | toggle |  | true | true
Output.ExhaustSpeed | enum | 200 | 100 | % | Exhaust fan speed | Exhaust fan speed | 0 | 100 | unknown | picker |  | true | true
Output.InletSpeed | enum | 201 | 100 | % | Inlet fan speed | Inlet fan speed | 0 | 100 | unknown | picker |  | true | true
Output.AirHeatCap | enum | 202 | 100 | % | Air heater capacity | Air heater capacity | 0 | 100 | unknown | picker |  | true | true
Output.CenHeatCap | enum | 203 | 100 | % | Central heater capacity | Central heater capacity | 0 | 100 | unknown | picker |  | true | true
Output.CprCap | enum | 204 | 100 | % | Compresor capacity | Compresor capacity | 0 | 100 | unknown | picker |  | true | true
Output.PreHeatCap | enum | 205 | 100 | % | Preheater capacity or earth tube air intake fan speed | Preheater capacity or earth tube air intake fan speed | 0 | 100 | unknown | picker |  | true | true
Time.Second | enum | 300 |  | ss | Second | Second | 0 | 59 | unknown | picker |  | true | true
Time.Minute | enum | 301 |  | nn | Minute | Minute | 0 | 59 | unknown | picker |  | true | true
Time.Hour | enum | 302 |  | hh | Hour | Hour | 0 | 23 | unknown | picker |  | true | true
Time.Day | enum | 303 |  | dd | Day | Day | 1 | 31 | unknown | picker |  | true | true
Time.Month | enum | 304 |  | mm | Month | Month | 1 | 12 | unknown | picker |  | true | true
Time.Year | enum | 305 |  | yyyy | Year | Year | 2024 | 2099 | unknown | picker |  | true | true
Alarm.Reset | enum | 400 |  |  | Clear alarm code or all 0 | Clear one specific alarm code or all 0 : No command, 1..99 : (reserved internal commands) 101..199 : Clear alarm display code 1..99 255 : Clear all alarms | 0 | 255 | unknown | picker |  | true | true
Program.Select | enum | 500 |  |  | Week program nb. select | Week program nb. select | 0 | 4 | unknown | picker | ["None","Program 1", "Program 2", "Program 3", "Erase"] | true | true
Program.UserFuncAct | enum | 600 |  |  | User function active (See “UserFuncSet”) | User function active (See “UserFuncSet”) | 0 | 6 | unknown | picker | ["None","Exend","Inlet","Exhaust","External heater offset","Ventilate","Cooker Hood"] | true | true
Program.UserFuncSet | enum | 601 |  |  | User function select | User function select | 0 | 6 | unknown | picker | ["None","Exend","Inlet","Exhaust","External heater offset","Ventilate","Cooker Hood"] | true | true
Program.UserTimeSet | enum | 602 |  | Min | User function period | User function period |  |  | unknown | picker |  | true | true
Program.UserVentSet | enum | 603 |  | Step | User function ventilation step select 0 : Off | User function ventilation step select 0 : Off | 0 | 4 | unknown | picker | ["OFF","1","2","3","4"] | true | true
Program.UserTempSet | enum | 604 |  | °C | User function temperature (Extend function only) | User function temperature (Extend function only) |  |  | unknown | picker |  | true | true
Program.UserOffsSet | enum | 605 |  | °C | User function temperature offset (Offset function only) | User function temperature offset (Offset function only) |  |  | unknown | picker |  | true | true
Program.User2FuncAct | enum | 610 |  |  | User function active (See “UserFuncSet”) | User function active (See “UserFuncSet”) | 0 | 6 | unknown | picker | ["None","Exend","Inlet","Exhaust","External heater offset","Ventilate","Cooker Hood"] | true | true
Program.User2FuncSet | enum | 611 |  |  | User2function select | User2function select | 0 | 6 | unknown | picker | ["None","Exend","Inlet","Exhaust","External heater offset","Ventilate","Cooker Hood"] | true | true
Program.User2TimeSet | enum | 612 |  |  | User2 function period | User2 function period |  |  | unknown | picker |  | true | true
Program.User2VentSet | enum | 613 |  |  | User2 function ventilation step select 0 : Off | User2 function ventilation step select 0 : Off | 0 | 4 | unknown | picker | ["OFF","1","2","3","4"] | true | true
Program.User2TempSet | enum | 614 |  |  | User2 function temperature (Extend function only) | User2 function temperature (Extend function only) |  |  | unknown | picker |  | true | true
Program.User2OffsSet | enum | 615 |  |  | User2 function temperature offset (Offset function only) | User2 function temperature offset (Offset function only) |  |  | unknown | picker |  | true | true
Log.Interval | enum | 700 |  | Min | Periodic log interval | Periodic data log interval select 0: Off 1..120: Time between periodic loggings | 0 | 120 | unknown | picker |  | true | true
Control.Type | enum | 1000 |  |  | Machine type | Machine type select (factory setting) |  |  | unknown | picker |  | true | true
Control.RunSet | enum | 1001 |  | OnOff | User on/off | User on / off select (equal to ON/OFF keys) |  |  | unknown | picker |  | true | true
Control.ModeSet | enum | 1002 |  |  | User operation mode | User operation mode select | 0 | 4 | unknown | picker | ["Off","Heat","Cool","Auto","Service (readonly)"] | true | true
Control.VentSet | enum | 1003 |  | Step | User ventilation step | User ventilation step select 0 : Off, 1-4 | 0 | 4 | unknown | picker | ["Off","1","2","3","4"] | true | true
Control.TempSet | number | 1004 | 100 | °C | User temperature setpoint | User temperature setpoint |  |  | target_temperature | thermostat |  | true | true
Control.ServiceMode | enum | 1005 |  |  | Service mode select | Service mode select | 0 | 8 | thermostat_mode | picker | ["Off","Defrost","Flaps","Inlet","Exhaust","Compressor","Heating","Hot water","Central heat"] | true | true
Control.ServicePct | enum | 1006 | 100 | % | Service mode capacity setpoint | Service mode capacity setpoint |  |  | unknown | picker |  | true | true
Control.Preset | enum | 1007 |  |  | Request preset to default settings | Request preset to default settings | 0 | 3 | thermostat_mode | picker | ["Ready","Standard (to factory defaults)","Backup (to user file)","Restore (from user file)"] | true | true
AirFlow.AirExchMode | enum | 1100 |  |  | Air exchange mode | Air exchange mode | 0 | 2 | thermostat_mode | picker | ["Energy","Comfort","ComfortWater"] | true | true
AirFlow.CoolVent | enum | 1101 |  | Step | Cooling high ventilation | Cooling high ventilation step | 0 | 4 | thermostat_mode | picker | ["Off","1","2","3","4"] | true | true
AirFlow.TestSelect | enum | 1102 |  |  | air damper self-test | Select a day for weekly air damper position self-test The test runs at 10 in the morning on the selected day Once enabled, the function cannot be deactivated | 0 | 7 | thermostat_mode | picker | ["OFF","Monday","Tuesday","Wednesday","Thursday","Friday","Saturday","Sunday"] | true | true
AirFlow.LastTestDay | enum | 1103 |  |  | Date of last air damper position test Bit word packed in DOS date format (see IR 402 format) | Date of last air damper position test Bit word packed in DOS date format (see IR 402 format) |  |  | unknown | picker |  | true | true
AirFlow.TestState | enum | 1104 |  |  | Actual air damper test | Actual air damper position test state 0: Off | 0 | 6 | thermostat_mode | picker | ["Off","Standby","Start","Closing","Opening","OK","Error"] | true | true
AirFlow.FiltAlmType | enum | 1105 |  |  | Air filter alarm | Air filter monitoring alarm type and period select 0: Pressure guard (input) | 0 | 5 | thermostat_mode | picker | ["Pressure guard (input)","30 days","90 days","180 days","360 days","70 days and pressure guard"] | true | true
AirTemp.CoolSet | enum | 1200 |  |  | Cooling temperature select | Cooling temperature setpoint select | 0 | 8 | thermostat_mode | picker | ["Off (No cooling allowed)","Set +0 °C","Set +1 °C","Set +2 °C","Set +3 °C","Set +4 °C","Set +5 °C","Set +7 °C","Set +10 °C"] | true | true
AirTemp.TempMinSum | number | 1201 | 100 | °C | Inlet temp. min. summer | Inlet temp. min. summer |  |  | target_temperature | thermostat |  | true | true
AirTemp.TempMinWin | number | 1202 | 100 | °C | Inlet temp. min. winter | Inlet temp. min. winter |  |  | target_temperature | thermostat |  | true | true
AirTemp.TempMaxSum | number | 1203 | 100 | °C | Inlet temp. max. summer | Inlet temp. max. summer |  |  | target_temperature | thermostat |  | true | true
AirTemp.TempMaxWin | number | 1204 | 100 | °C | Inlet temp. max. winter | Inlet temp. max. winter |  |  | target_temperature | thermostat |  | true | true
AirTemp.TempSummer | number | 1205 | 100 | °C | Summer/winter limit | Summer/winter limit |  |  | target_temperature | thermostat |  | true | true
AirTemp.NightDayLim | number | 1206 | 100 | °C | Outdoor day temperature for night cooling activation [0:Off, 20..40] | Outdoor day temperature for night cooling activation [0:Off, 20..40] | 0 | 40 | target_temperature | thermostat |  | true | true
AirTemp.NightSet | number | 1207 | 100 | °C | Free energy night cooling room setpoint [10..30] | Free energy night cooling room setpoint [10..30] | 10 | 30 | target_temperature | thermostat |  | true | true
AirTemp.SensorSelect | number | 1208 |  |  | Control temperature sensor select 0: User panel | Control temperature sensor select 0: User panel | 0 | 3 | target_temperature | thermostat | ["User panel","External sensor","Inlet channel","Exhaust channel"] | true | true
AirTemp.HeatSelect | enum | 1209 | 1 |  | Valg af varmekilde: 0=No heating active, 1=Heatpump only, 2=HP+afterheat, 3=Afterheat only, | Valg af varmekilde: 0=No heating active, 1=Heatpump only, 2=HP+afterheat, 3=Afterheat only, |  |  | unknown | thermostat_mode | ["No heating active","Heatpump only","HP+afheat","Afterheat only","Afterheat+HP"] | true | true
Compressor.CondTempMin | number | 1500 | 100 | °C | Low temperaturcurve. | Low temperaturcurve. |  |  | target_temperature | thermostat |  | true | true
Compressor.CondTempMax | number | 1501 | 100 | °C | High temperaturcurve | High temperaturcurve |  |  | target_temperature | thermostat |  | true | true
AirTemp.TempMinCpr | number | 1502 | 100 | °C | Low temperature compressor start | Low temperature compressor start |  |  | target_temperature | thermostat |  | true | true
AirTemp.CprRestart | enum | 1503 | 60 |  | Compressor stop time | Compressor stop time |  |  | unknown | picker |  | true | true
HotWater.TempSet_T11 | number | 1700 | 100 | °C | Top temperature setpoint (electric) | Top temperature setpoint (electric) |  |  | target_temperature | thermostat |  | true | true
HotWater.TempSet_T12 | number | 1701 | 100 | °C | Bottom temperature setpoint (compressor) | Bottom temperature setpoint (compressor) |  |  | target_temperature | thermostat |  | true | true
HotWater.Priority | enum | 1702 | 1 |  | Priority: 0=Water, 1=Inlet | Priority: 0=Water, 1=Inlet | 0 | 1 | thermostat_mode | picker | ["Water","Inlet"] | true | true
HotWater.TempCprMax | number | 1703 | 100 | °C | Scald protection Temperature | Scald protection Temperature |  |  | target_temperature | thermostat |  | true | true
HotWater.HeatType | enum | 1704 | 1 |  | Use of supplement: | Use of electricity supplement: |  |  | thermostat_mode | picker | ["Off","Electricity] | true | true
HotWater.LegioType | enum | 1705 | 1 |  | Day for legionella: | Day for legionella: | 0 | 7 | thermostat_mode | picker | ["OFF","Monday","Tuesday","Wednesday","Thursday","Friday","Saturday","Sunday"] | true | true
HotWater.TempPri | enum | 1706 | 1 | °C | Bypass offset: 0=Off, 1..30°C | Bypass offset: 0=Off, 1..30°C | 0 | 30 | unknown | picker |  | true | true
CentralHeat.HeatExtern | enum | 1800 | 100 | °C | External heating offset from room temperature setpoint | External heating offset from room temperature setpoint |  |  | unknown | picker |  | true | true
CentralHeat.HeatSelect | enum | 1801 | 1 |  | 0=Only Pump motion and freze secure, 1=Always central heating, | 0=Only Pump motion and freze secure, 1=Always central heating, |  |  | unknown | picker |  | true | true
CentralHeat.SupplyMin | enum | 1802 | 100 | °C | Min supply temperature | Min supply temperature |  |  | unknown | picker |  | true | true
CentralHeat.SupplyMax | enum | 1803 | 100 | °C | Max supply temperature | Max supply temperature |  |  | unknown | picker |  | true | true
CentralHeat.SupplyOffset | enum | 1804 | 100 | °C | Outdoor temperature compensation | Outdoor temperature compensation |  |  | unknown | picker |  | true | true
CentralHeat.CurveSelect | enum | 1805 | 1 |  | Temp. compensation curve: 1-10 | Temp. compensation curve: 1-10 |  |  | unknown | picker |  | true | true
CentralHeat.CircPumpMode | enum | 1806 | 1 |  | 0=Only when heating is active, 1=Continuous operation | 0=Only when heating is active, 1=Continuous operation |  |  | unknown | picker |  | true | true
CentralHeat.HeatType | enum | 1807 | 1 |  | 0=OFF, | 0=OFF, |  |  | unknown | picker |  | true | true
CentralHeat.RegTime | enum | 1808 | 1 | Sec | PID regulations time: 0=2sec, 1-25(sec) | PID regulations time: 0=2sec, 1-25(sec) |  |  | unknown | picker |  | true | true
AirQual.RH_VentLo | enum | 1910 |  | Step | Humidity low winter step select | Humidity low winter step select |  |  | unknown | picker |  | true | true
AirQual.RH_VentHi | enum | 1911 |  | Step | Humidity high step select | Humidity high step select |  |  | unknown | picker |  | true | true
AirQual.RH_LimLo | enum | 1912 | 100 | % | Humidity limit for low ventilation | Humidity limit for low ventilation |  |  | unknown | picker |  | true | true
AirQual.RH_TimeOut | enum | 1913 |  | min | Humidity max. time on high ventilation | Humidity max. time on high ventilation |  |  | unknown | picker |  | true | true
AirQual.CO2_VentHi | enum | 1920 |  | Step | CO2 high step select | CO2 high step select |  |  | unknown | picker |  | true | true
AirQual.CO2_LimLo | enum | 1921 |  | ppm | CO2 limit for normal ventilation | CO2 limit for normal ventilation |  |  | unknown | picker |  | true | true
AirQual.CO2_LimHi | enum | 1922 |  | ppm | CO2 limit for high ventilation | CO2 limit for high ventilation |  |  | unknown | picker |  | true | true
User. UserMenuOpen | enum | 2002 |  |  | Menu is open: | Menu is open: |  |  | unknown | picker |  | true | true
User.Language | enum | 2003 | 1 |  | HMI language | HMI language | 0 | 9 | unknown | picker | ["English","German","French","Swedish","Danish","Norwegian","Finish","Czech","Polish","Italian"] | true | true
PreHeat.Block | enum | 2100 |  |  | COMFORT(n) only | COMFORT(n) only |  |  | unknown | picker |  | true | true
DPT.DoCalibrate | enum | 2200 |  | 0.1 | Calibrate DPT. | Calibrate DPT. |  |  | unknown | picker |  | true | true
| enum |  |  |  | 1: Start calibration | 1: Start calibration |  |  | unknown | picker |  | true | true
CentralHeat.HeatExtern | enum | 4000 | 100 | °C | Regulation deadband external room heating | Regulation deadband external room heating | -5 | 5 | unknown | picker |  | true | true
AirFlow.CoolVent | enum | 4001 |  |  | High fan speed at high indoor temp (cooling demand) Level OFF, 2-4 | High fan speed at high indoor temp (cooling demand) Level OFF, 2-4 |  |  | unknown | picker |  | true | true
AirFlow.WinterTemp | enum | 4002 | 1 | °C | Low outdoor temperature | Low outdoor temperature | -20 | 10 | unknown | picker |  | true | true
| enum |  |  |  | -20°C - 10°C | -20°C - 10°C |  |  | unknown | picker |  | true | true
AirFlow.WinerVent | enum | 4003 |  |  | Fan speed at low outdoor temperature 0: OFF | Fan speed at low outdoor temperature 0: OFF | 0 | 3 | thermostat_mode | picker | ["OFF","1","2","3"] | true | true
AirFlow.TestSelect | enum | 4004 |  |  | Day for automatic test 0: OFF | Day for automatic test 0: OFF | 0 | 7 | thermostat_mode | picker | ["OFF","Monday","Tuesday","Wednesday","Thursday","Friday","Saturday","Sunday"] | true | true
AirHeat.Type | enum | 4005 |  |  | After heating type | After heating type | 0 | 3 | thermostat_mode | picker | ["No additional heat","Electrical","Electric on binary relays","Water"] | true | true
AirHeat.Delay | enum | 4006 | 1 | Min | Delay timer for after-heat activation 0-60 min. | Delay timer for after-heat activation 0-60 min. |  |  | unknown | picker |  | true | true
AirTemp.TempMinSum | enum | 4007 | 100 | °C | Summer minimum supply air temperature MinSum: 5.00-14.00 | Summer minimum supply air temperature MinSum: 5.00-14.00 |  |  | unknown | picker |  | true | true
AirTemp.TempMaxSum | enum | 4008 | 100 | °C | Summer maximum supply air temperature MaxSum: 5.00-25.00 | Summer maximum supply air temperature MaxSum: 5.00-25.00 |  |  | unknown | picker |  | true | true
AirTemp.TempMinWin | enum | 4009 | 100 | °C | Winter minimum supply air temperature MinWin: 5.00-16.00 | Winter minimum supply air temperature MinWin: 5.00-16.00 |  |  | unknown | picker |  | true | true
AirTemp.TempMaxWin | enum | 4010 | 100 | °C | Winter maximum supply air temperature MaxWin: 5.00-35.00 | Winter maximum supply air temperature MaxWin: 5.00-35.00 |  |  | unknown | picker |  | true | true
AirTemp.RoomNZ | enum | 4011 | 100 |  | Room temperature regulation deadband | Room temperature regulation deadband |  |  | unknown | picker |  | true | true
| enum |  |  |  | 0.20 – 10.00 | 0.20 – 10.00 |  |  | unknown | picker |  | true | true
AirTemp.TempRoomLow | enum | 4012 | 100 | °C | Low room temperature for stepwise reduced ventilation 0: OFF | Low room temperature for stepwise reduced ventilation 0: OFF | 1 | 20 | unknown | picker |  | true | true
AirHeat.SelectSet | enum | 4013 |  |  | After heating activation: | After heating activation: |  |  | unknown | picker | ["Off","On (No effect if Airheat is off)"] | true | true
| enum |  |  |  | 0: Off | 0: Off |  |  | unknown | picker |  | true | true
| enum |  |  |  | 1: On (No effect is AirHeat.Type (H4005) is 0.) | 1: On (No effect is AirHeat.Type (H4005) is 0.) |  |  | unknown | picker |  | true | true
AirFlow.InletMin | enum | 4015 | 1 |  | Min. inlet: 0-2 | Min. inlet: 0-2 | 0 | 2 | unknown | picker |  | true | true
AirFlow.ExhaustMin | enum | 4016 | 1 |  | Min exhaust: 1-2 | Min exhaust: 1-2 | 1 | 2 | unknown | picker |  | true | true
AirFlow.ExhaustMax | enum | 4017 | 1 |  | Max exhaust: | Max exhaust: |  |  | unknown | picker |  | true | true
AirFlow.StartDelay | enum | 4018 | 60 |  | Start delay | Start delay |  |  | unknown | picker |  | true | true
AirBypass.WalkingTime | enum | 4019 | 1 | Sec | Damper walkin time: 60-900 sec. | Damper walkin time: 60-900 sec. |  |  | unknown | picker |  | true | true
Defrost.Fans | enum | 4020 |  |  | Frost protection or de-icing - Ventilation level 0: OFF | Frost protection or de-icing - Ventilation level 0: OFF |  |  | unknown | picker | ["OFF","USER","LOW"] | true | true
Defrost.Bypass | enum | 4021 |  |  | Frost protection or de-icing - Bypass position 0: OFF | Frost protection or de-icing - Bypass position 0: OFF |  |  | unknown | picker | ["OFF","ON"] | true | true
Defrost.BlockMinutes | enum | 4022 | 1 | Min | Frost protection or de-icing - Time between activations 15 - 720 | Frost protection or de-icing - Time between activations 15 - 720 |  |  | unknown | picker |  | true | true
Defrost.TempStart | number | 4023 | 100 | °C | Frost protection or de-icing - Start criteria | Frost protection or de-icing - Start criteria | -10 | 0 | target_temperature | thermostat |  | true | true
Defrost.TempStop | number | 4024 | 100 | °C | Frost protection or de-icing - Stop criteria 2.00°C – 12.00°C | Frost protection or de-icing - Stop criteria 2.00°C – 12.00°C | 2 | 12 | target_temperature | thermostat |  | true | true
Defrost.DurMaxCpr | enum | 4025 | 1 | Min | Frost protection or de-icing - Max duration compressor 2 – 60 | Frost protection or de-icing - Max duration compressor 2 – 60 | 2 | 60 | unknown | picker |  | true | true
Defrost.DurMaxExh | enum | 4026 | 1 | Min | Frost protection or de-icing - Max duration exchanger 5 – 60 | Frost protection or de-icing - Max duration exchanger 5 – 60 | 5 | 60 | unknown | picker |  | true | true
Defrost.T6MinRunSec | enum | 4027 | 1 | Sec | T6 min defrost time: 10-120sec. | T6 min defrost time: 10-120sec. | 10 | 120 | unknown | picker |  | true | true
Program.EditIndex | enum | 4030 |  |  | Week program - Index: 0-41 (7 days multiply by 6 functions each day) | Week program - Index: 0-41 (7 days multiply by 6 functions each day) | 0 | 41 | unknown | picker |  | true | true
Program.EditPeriod | enum | 4031 |  |  | Week program | Week program |  |  | unknown | picker | ["Monday","Tuesday","Wednesday","Thursday","Friday","Saturday","Sunday"] | true | true
Program.EditPeriodNx | enum | 4032 |  |  | Week program | Week program |  |  | unknown | picker | ["Monday","Tuesday","Wednesday","Thursday","Friday","Saturday","Sunday"] | true | true
Program.EditFunc | enum | 4033 |  |  | Week program Day function 0-5. | Week program Day function 0-5. | 0 | 5 | unknown | picker |  | true | true
Program.EditTimeStar | enum | 4034 |  |  | Week program start time (1215 = 12:15) | Week program start time (1215 = 12:15) | 0 | 2345 | unknown | picker |  | true | true
Program.EditVent | enum | 4035 |  |  | Week program Fan settings: 0-4 0=Off, | Week program Fan settings: 0-4 0=Off, |  |  | unknown | picker | ["OFF","1","2","3","4"] | true | true
Program.EditTemp | enum | 4036 | 1 | °C | Week program Temperature: 5°C - 50°C | Week program Temperature: 5°C - 50°C | 5 | 50 | unknown | picker |  | true | true
Control.RestartMode | enum | 4040 |  |  | External fire alarm auto reset 0: OFF | External fire alarm auto reset 0: OFF | 0 | 3 | unknown | picker | ["OFF", "HPLP", "CONTINUE", "SELF_CLEAR"] | true | true
Control.PowerSave | boolean | 4041 |  |  | Enable power saving | Enable power saving features 0: OFF |  |  | onoff | toggle |  | true | true
Alarm.LogIndex | enum | 4050 |  |  | Alarm log index 0 - 15 | Alarm log index 0 - 15 |  |  | unknown | picker |  | true | true
AirFlow.InletScale | enum | 4098 |  | % | Scaling of inlet fan control voltage for max. air volume Range: 50..100 | Scaling of inlet fan control voltage for max. air volume Range: 50..100 | 50 | 100 | unknown | picker |  | true | true
AirFlow.ExhaustScale | enum | 4099 |  | % | Scaling of exhaust fan control voltage for max. air volume Range: 50..100 | Scaling of exhaust fan control voltage for max. air volume Range: 50..100 | 50 | 100 | unknown | picker |  | true | true
AirFlow.InletSpd_1 | enum | 4100 |  |  | Inlet step 1 speed setup Range: 20..100 | Inlet step 1 speed setup Range: 20..100 | 20 | 100 | unknown | picker |  | true | true
AirFlow.InletSpd_2 | enum | 4101 |  |  | Inlet step 2 speed setup Range: 20..100 | Inlet step 2 speed setup Range: 20..100 | 20 | 100 | unknown | picker |  | true | true
AirFlow.InletSpd_3 | enum | 4102 |  |  | Inlet step 3 speed setup Range: 20..100 | Inlet step 3 speed setup Range: 20..100 | 20 | 100 | unknown | picker |  | true | true
AirFlow.InletSpd_4 | enum | 4103 |  |  | Inlet step 4 speed setup Range: 20..100 | Inlet step 4 speed setup Range: 20..100 | 20 | 100 | unknown | picker |  | true | true
AirFlow.ExhaustSpd_1 | enum | 4104 |  |  | Exhaust step 1 speed setup Range: 20..100 | Exhaust step 1 speed setup Range: 20..100 | 20 | 100 | unknown | picker |  | true | true
AirFlow.ExhaustSpd_2 | enum | 4105 |  |  | Exhaust step 2 speed setup Range: 20..100 | Exhaust step 2 speed setup Range: 20..100 | 20 | 100 | unknown | picker |  | true | true
AirFlow.ExhaustSpd_3 | enum | 4106 |  |  | Exhaust step 3 speed setup Range: 20..100 | Exhaust step 3 speed setup Range: 20..100 | 20 | 100 | unknown | picker |  | true | true
AirFlow.ExhaustSpd_4 | enum | 4107 |  |  | Exhaust step 4 speed setup Range: 20..100 | Exhaust step 4 speed setup Range: 20..100 | 20 | 100 | unknown | picker |  | true | true
AirQual.Type | enum | 4108 |  |  | Enable Indoor Air Quality (IAQ) control function Range: 0..2 | Enable Indoor Air Quality (IAQ) control function Range: 0..2 | 0 | 2 | unknown | picker |  | true | true
Control.AnaOutType | enum | 4109 |  |  | Heater output signal type (if not air channel type) Range: 0..4 | Heater output signal type (if not air channel type) Range: 0..4 | 0 | 4 | unknown | picker |  | true | true
AirTemp.RoomResponse | enum | 4110 |  |  | Room temperature controller response type Select predefined or user adjustable parameters Range: 0..3 | Room temperature controller response type Select predefined or user adjustable parameters Range: 0..3 | 0 | 3 | unknown | picker |  | true | true
PreHeat.Defrost | enum | 4111 |  |  | Nordic: Select anti frost also during evap. defrost COMFORT: Select T8 preheater allowance on R5 Range: 0..1 | Nordic: Select anti frost also during evap. defrost COMFORT: Select T8 preheater allowance on R5 Range: 0..1 | 0 | 1 | unknown | picker |  | true | true
PreHeat.TempSet | enum | 4112 |  |  | T4 start criteria when temperature controlled exchanger defrosting is selected (without no-frost) Range: 0..5 | T4 start criteria when temperature controlled exchanger defrosting is selected (without no-frost) Range: 0..5 | 0 | 5 | unknown | picker |  | true | true

## Utils
on | yes | open | true
off | no | closed | false

## Classes
Name | ID | Description | Allows Virtual
Amplifier | amplifier | Use this device class for audio amplifier devices. | no
Blinds | blinds | Use this device class for blinds, both horizontal and vertical. | no
Button | button | Use this device class for buttons, such as a remote. | no
Camera | camera | Security camera | no
Coffee machine | coffeemachine | Use this device class for coffee machines. | no
Curtains | curtain | Use this device class for curtains. | no
Doorbell | doorbell | Use this device class for doorbells, usually together with the `button` capability. | no
Fan | fan | Use this device class for fans that cool your home. | no
Garage door | garagedoor | Use this device class for garage doors, usually together with the `garagedoor_closed` capability. | no
Heater | heater | Use this device class for heaters, that warm your home. | no
Home Security | homealarm | Use this device class for home alarm systems. | no
Kettle | kettle | Use this device class for kettle devices, that can heat water. | no
Light | light | Use this device class for lights, usually together with the `onoff`, `dim` and `light_*` capabilities. | no
Lock | lock | Use this device class for lock devices, usually together with the `locked` and `lock_mode` capabilities. | no
Other | other | Use this device class for devices that do not fit any other device class. | no
Remote | remote | Use this device class for (TV/Sunblind/Keyfob etc.) remotes. | no
Sensor | sensor | Use this device class for sensors, e.g. a contact or motion sensor. | no
Wall Plug | socket | Use this device class for sockets (built-in or plug-in socket switches). When adding the `choose_slave` pair template, the user is presented a `What's plugged in?` question. | yes
Speaker | speaker | Use this device class for devices that can play music, usually together with the `speaker_*` capabilities. | no
Solar Panel | solarpanel | Use this device class for solar panels. | no
Sunshade | sunshade | Use this device class for sunshades (window coverings against the sun). | no
Thermostat | thermostat | Use this device class for thermostats, either for the entire home or radiator-mounted, usually together with the `measure_temperature`, `target_temperature` and `thermostat_mode` capabilities. | no
TV | tv | Use this device class for TVs. | no
Vacuum Cleaner | vacuumcleaner | Use this device class for vacuum cleaners, usually together with the `vacuumcleaner_state` capability. | no
Window Coverings | windowcoverings | Use this device class for window coverings, when the `curtains`, `blinds` or `sunshade` device class doesn't apply. | yes
yes
no

## Capabilities
Name | order | ID | Type | Getable | Setable | Insights | Quick Action | Flow | UI Component
Unknown | 73 | unknown | number | true | false | false | false | false | media
Battery alarm | 40 | alarm_battery | boolean | true | false | true | false | true | battery
CO alarm | 32 | alarm_co | boolean | true | false | true | false | true | sensor
CO2 alarm | 33 | alarm_co2 | boolean | true | false | true | false | true | sensor
Contact alarm | 31 | alarm_contact | boolean | true | false | true | false | true | sensor
Fire alarm | 37 | alarm_fire | boolean | true | false | true | false | true | sensor
Generic alarm | 29 | alarm_generic | boolean | true | false | true | false | true | sensor
Heat alarm | 38 | alarm_heat | boolean | true | false | true | false | true | sensor
Motion alarm | 30 | alarm_motion | boolean | true | false | true | false | true | sensor
Night alarm | 41 | alarm_night | boolean | true | false | true | false | true | sensor
PM2.5 alarm | 34 | alarm_pm25 | boolean | true | false | true | false | true | sensor
Smoke alarm | 36 | alarm_smoke | boolean | true | false | true | false | true | sensor
Tamper alarm | 35 | alarm_tamper | boolean | true | false | true | false | true | sensor
Water alarm | 39 | alarm_water | boolean | true | false | true | false | true | sensor
Button | 62 | button | boolean | false | true | false | true | true | button
Channel down | 52 | channel_down | boolean | false | true | false | false | true | button
Channel up | 51 | channel_up | boolean | false | true | false | false | true | button
Dim level | 2 | dim | number | true | true | false | false | true | slider
Closed | 55 | garagedoor_closed | boolean | true | true | false | false | true | toggle
Home alarm state | 46 | homealarm_state | enum | true | true | false | false | true | picker
Hue | 3 | light_hue | number | true | true | false | false | true | color
Light mode | 6 | light_mode | enum | true | true | true | false | false | color
Color saturation | 4 | light_saturation | number | true | true | true | false | true | color
Color temperature | 5 | light_temperature | number | true | true | true | false | true | color
Lock mode | 54 | lock_mode | enum | true | true | false | false | true | picker
Locked | 53 | locked | boolean | true | true | true | false | true | toggle
Battery | 22 | measure_battery | number | true | false | true | false | true | battery
CO | 11 | measure_co | number | true | false | true | false | true | sensor
CO2 | 12 | measure_co2 | number | true | false | true | false | true | sensor
Current | 25 | measure_current | number | true | false | true | false | true | sensor
Gust angle | 21 | measure_gust_angle | number | true | false | true | false | true | sensor
Gust strength | 20 | measure_gust_strength | number | true | false | true | false | true | sensor
Humidity | 14 | measure_humidity | number | true | false | true | false | true | sensor
Luminance | 26 | measure_luminance | number | true | false | true | false | true | sensor
Noise | 16 | measure_noise | number | true | false | true | false | true | sensor
PM2.5 | 13 | measure_pm25 | number | true | false | true | false | true | sensor
Power | 23 | measure_power | number | true | false | true | false | true | sensor
Pressure | 15 | measure_pressure | number | true | false | true | false | true | sensor
Rain | 17 | measure_rain | number | true | false | true | false | true | sensor
Temperature | 10 | measure_temperature | number | true | false | true | false | true | sensor
Ultraviolet | 27 | measure_ultraviolet | number | true | false | true | false | true | sensor
Voltage | 24 | measure_voltage | number | true | false | true | false | true | sensor
Water flow | 28 | measure_water | number | true | false | true | false | true | sensor
Wind angle | 19 | measure_wind_angle | number | true | false | true | false | true | sensor
Wind strength | 18 | measure_wind_strength | number | true | false | true | false | true | sensor
Gas meter | 44 | meter_gas | number | true | false | true | false | true | sensor
Energy | 42 | meter_power | number | true | false | true | false | true | sensor
Rain meter | 45 | meter_rain | number | true | false | true | false | true | sensor
Water meter | 43 | meter_water | number | true | false | true | false | true | sensor
Turned on | 1 | onoff | boolean | true | true | false | true | true | toggle
Album | 69 | speaker_album | string | true | false | false | false | true | media
Artist | 68 | speaker_artist | string | true | false | false | false | true | media
Duration | 71 | speaker_duration | number | true | false | false | false | false | media
Next | 64 | speaker_next | boolean | false | true | false | false | true | media
Playing | 63 | speaker_playing | boolean | true | true | false | true | true | media
Position | 72 | speaker_position | number | true | false | false | false | false | media
Previous | 65 | speaker_prev | boolean | false | true | false | false | true | media
Repeat | 67 | speaker_repeat | enum | true | true | false | false | true | media
Shuffle | 66 | speaker_shuffle | boolean | true | true | false | false | true | media
Track | 70 | speaker_track | string | true | false | false | false | true | media
Target temperature | 9 | target_temperature | number | true | true | true | false | true | thermostat
Thermostat mode | 8 | thermostat_mode | enum | true | true | true | false | true | picker
Vacuum cleaner state | 7 | vacuumcleaner_state | enum | true | true | true | false | true | picker
Volume down | 49 | volume_down | boolean | false | true | false | false | true | button
Volume muted | 50 | volume_mute | boolean | true | true | false | false | true | button
Set volume | 47 | volume_set | number | true | true | false | false | true | slider
Volume up | 48 | volume_up | boolean | false | true | false | false | true | button
Closed | 60 | windowcoverings_closed | boolean | true | true | false | false | true | toggle
Position | 61 | windowcoverings_set | number | true | true | false | false | true | slider
Window coverings state | 56 | windowcoverings_state | enum | true | true | false | false | true | ternary
Window coverings tilt down | 58 | windowcoverings_tilt_down | boolean | false | true | false | false | false | button
Window coverings tilt set | 59 | windowcoverings_tilt_set | number | true | true | false | false | false | slider
Window coverings tilt up | 57 | windowcoverings_tilt_up | boolean | false | true | false | false | false | button

## HoldingOverview
Name | Address | RegCount | Description
Bus | 50 | 1 | Bus adressing
Output1 | 100 | 28 | Output registers - 1
Output2 | 200 | 6 | Output registers - 2
Time | 300 | 6 | Clock and calendar
Alarm | 400 | 1 | Alarm and message handling
Week program | 500 | 1 | Calendar based programming
User functions | 600 | 6 | User input function selection
User 2 functions | 610 | 6 | User 2 input function selection
Data log | 700 | 1 | Data, alarm and event logging
Control | 1000 | 8 | System control and status
AirFlow | 1100 | 6 | Ventilation control
AirTemp | 1200 | 10 | Room temperature control
Compressor | 1500 | 4 | Compressor operation control
HotWater | 1700 | 7 | Hot water control
CentHeat | 1800 | 9 | Central heating control (EK)
AirQual | 1900 | 23 | Air quality control (RH, CO2)
User panel | 2002 | 2 | Display and keyboard
PreHeat | 2100 | 1 | Intake air preheat / earth tube
DPT | 2200 | 1 | Difference pressure transducer
Defrost | 4000 | 28 | Defrost
Program | 4030 | 7 | Weekly program
Control | 4040 | 2 | Control
Alarm | 4050 | 1 | Alarm
AirFlow | 4098 | 10 | Airflow
AirQuality | 4108