## InputOverview
Name | Address | RegCount | Description
Device | 0 | 6 | Protocol and controller setup
DiscreteIO | 100 | 17 | Input / output bits (on/off)
AnalogIO | 200 | 23 | Input / output words
Time | 300 |  | Clock and calendar
Alarm | 400 | 10 | Alarm and message handling
WeekProgram | 500 |  | Calendar based programming
UserFunctions | 600 |  | User input function selection
DataLog | 700 |  | Data, alarm and event logging
Control | 1000 | 4 | System control and status
AirFlow | 1100 | 5 | Ventilation control
AirTemp | 1200 | 7 | Room temperature control
AirBypass | 1300 |  | Exchanger bypass control
AirHeat | 1400 |  | Inlet air heater control
Compressor | 1500 | 1 | Compressor operation control
Defrost | 1600 |  | Defrosting control
HotWater | 1700 | 2 | Hot water control
CentHeat | 1800 | 1 | Central heating control (EK)
AirQual | 1900 |  | Air quality control (RH, CO2)
UserPanel | 2000 |  | Display and keyboard
PreHeat | 2100 | 1 | Intake air preheat / earth tube
DPT | 2200 | 3 | Difference pressure transducer
Display | 3000 | 10 | Display information
Alarm | 3050 | 26 | Alarm log
AirQuality | 3100 | 3 | Air quality display

## InputRegisters
Name | Address | Scale | Unit | Description | ID
Bus.Version | 0 |  |  | Protocol version number | speaker_playing
App.VersionMajor | 1 | text |  | Software version - major (2 character ascii text)
App.VersionMinor | 2 | text |  | Software version - minor (2 character ascii text)
App.VersionRelease | 3 | text |  | Software version - release (2 character ascii text)
Info.AppID | 4 |  |  | Application Id
Info.HWType | 5 |  |  | Application hardware Id
Input.UserFunc | 100 |  |  | User function
Input.AirFilter | 101 |  |  | Air filter alarm | onoff
Input.DoorOpen | 102 |  |  | Door contact | onoff
Input.Smoke | 103 |  |  | Smoke alarm | alarm_smoke
Input.MotorThermo | 104 |  |  | Motor thermo fuse | onoff
Input.Frost_Overht | 105 |  |  | Heating surface frost / overheat | onoff
Input.AirFlow | 106 |  |  | Airflow monitor | onoff
Input.P_HI | 107 |  |  | High pressure switch | onoff
Input.P_LO | 108 |  |  | Low pressure switch | onoff
Input.Boil | 109 |  |  | Hot water boiling
Input.3WayPos | 110 |  |  | Hot water 3-way valve position | onoff
Input.DefrostHG | 111 |  |  | Hotgas defrost type selection | onoff
Input.Defrost | 112 |  |  | Defrost thermostat | onoff
Input.UserFunc_2 | 113 |  |  | User function 2
Input.DamperClosed | 114 |  |  | Air damper closed position switch | onoff
Input.DamperOpened | 115 |  |  | Air damper opened position switch | onoff
Input.FCorThermoAl | 116 |  |  | Combined FC and thermo alarm | onoff
Input.T0_Controller | 200 | 100 | °C | Controller board temperature | measure_temperature
Input.T1_Intake | 201 | 100 | °C | Fresh air intake temperature | measure_temperature
Input.T2_Inlet | 202 | 100 | °C | Inlet temperature (before heater) | measure_temperature
Input.T3_Exhaust | 203 | 100 | °C | Room exhaust temperature | measure_temperature
Input.T4_Outlet | 204 | 100 | °C | Outlet temperature | measure_temperature
Input.T5_Cond | 205 | 100 | °C | Condenser temperature | measure_temperature
Input.T6_Evap | 206 | 100 | °C | Evaporator temperature | measure_temperature
Input.T7_Inlet | 207 | 100 | °C | Inlet temperature (after heater) | measure_temperature
Input.T8_Outdoor | 208 | 100 | °C | Outdoor temperature | measure_temperature
Input.T9_Heater | 209 | 100 | °C | Heating surface temperature | measure_temperature
Input.T10_Extern | 210 | 100 | °C | External room temperature | measure_temperature
Input.T11_Top | 211 | 100 | °C | Hot water top temperature | measure_temperature
Input.T12_Bottom | 212 | 100 | °C | Hot water bottom temperature | measure_temperature
Input.T13_Return | 213 | 100 | °C | EK return temperature | measure_temperature
Input.T14_Supply | 214 | 100 | °C | EK supply temperature | measure_temperature
Input.T15_Room | 215 | 100 | °C | User panel room temperature | measure_temperature
Input.T16 | 216 | 100 | °C | AUX temperature (Hotwater anode) | measure_temperature
Input.T17_PreHeat | 217 | 100 | °C | Preheater or earth tube air intake temperature | measure_temperature
Input.T18_PresPibe | 218 | 100 | °C | Pressure pibe temperature | measure_temperature
Input.pSuc | 219 |  | bar | Suction pressure | measure_pressure
Input.pDis | 220 |  | bar | Dischage pressure | measure_pressure
AirQual.RH | 221 | 100 | % | Humidity sensor value | measure_humidity
AirQual.CO2 | 222 |  | ppm | Carbon dioxide sensor value
Alarm.Status | 400 |  |  | Alarm state bit mask
Alarm.List_1_ID | 401 |  |  | Alarm 1 - Code
Alarm.List_1_Date | 402 |  |  | Alarm 1 - Date
Alarm.List_1_Time | 403 |  |  | Alarm 1 - Time
Alarm.List_2_ID | 404 |  |  | Alarm 2 - Code
Alarm.List_2_Date | 405 |  |  | Alarm 2 - Date
Alarm.List_2_Time | 406 |  |  | Alarm 2 - Time
Alarm.List_3_ID | 407 |  |  | Alarm 3 - Code
Alarm.List_3_Date | 408 |  |  | Alarm 3 - Date
Alarm.List_3_Time | 409 |  |  | Alarm 3 - Time
Control.RunAct | 1000 |  |  | Actual on/off state
Control.ModeAct | 1001 |  |  | Actual operation mode
Control.StateDisplay | 1002 |  |  | Actual control state
Control.SecInState | 1003 |  | Sec | Actual time in state
AirFlow.VentSet | 1100 |  | Step | Actual ventilation step set point 0 : Off
AirFlow.InletAct | 1101 |  | Step | Actual inlet fan speed step 0 : Off
AirFlow.ExhaustAct | 1102 |  | Step | Actual exhaust fan speed step 0 : Off
AirFlow.SinceFiltDay | 1103 |  | Days | Days since last air filter change alarm
AirFlow.ToFiltDay | 1104 |  | Days | Days to next air filter change alarm
AirTemp.IsSummer | 1200 |  |  | Summer state
AirTemp.TempInletSet | 1201 | 100 | °C | Inlet temperature request (T7 setpoint)
AirTemp.TempControl | 1202 | 100 | °C | Actual value for controlled temperature
AirTemp.TempRoom | 1203 | 100 | °C | Actual room temperature (T15 or T10)
AirTemp.EffPct | 1204 | 100 | % | Passive heat exchanger efficiency calculation
AirTemp.CapSet | 1205 | 100 | % | Requested capacity
AirTemp.CapAct | 1206 | 100 | % | Actual capacity
Compressor.Type | 1500 |  | 0..2 | 0: None, 1: On/Off, 2: Modulated hotgas valve
HotWater.Type | 1700 |  | 0..3 | 0: None, 1:Only hotware (VGU), 2:With ventilation (VP), 3:With central heating (VGU180) | thermostat_mode
HotWater.AnodeState | 1701 |  | 0..3 | 0=OFF, 1=OK, 2=SERVICE, 3=ERROR | thermostat_mode
CentralHeat.HeatExtSet | 1800 | 100 | °C | Actual setpoint for external heating source | target_temperature
PreHeat.BlockRemain | 2100 |  | Sec | Remaining time for the pre-heater blocking function commanded by the HR 2100 register
DPT.InSession | 2200 | 0.1 |  | 1 if DPT node is in session
DPT.AirFlow1 | 2201 |  | m3/h | Calculated air flow 1
DPT.AirFlow2 | 2202 |  | m3/h | Calculated air flow 2
AirBypass.IsOpen | 3000 |  |  | Bypass damper 0: Closed
Output.AirHeatCap | 3001 | 100 | % | After heating element
Defrost.ExchDefrost | 3002 |  |  | De-icing heat exchanger 0: Off
AirQual.CO2_Enable | 3003 |  |  | CO2 sensor present in the system or not 0: Off | button
AirFlow.RoomReduce | 3004 |  |  | Stop at low room temperature 0-4
AirFlow.LastTestDay | 3005 |  |  | Date for last air damper self-test
AirFlow.SinceFiltDay | 3006 |  |  | Days since last air filter change
AirFLow.WinterReduce | 3007 |  |  | Low fan speed at low outdoor temperature Level 0-4
AirTemp.TempSet | 3008 | 100 | °C | Actual resulting set-point for room temperature 5.00°C - 50.00°C
AirTemp.TempControl | 3009 | 100 | °C | Master sensor for the controlled temperature (room / inlet) | measure_temperature
Alarm.LogEventID | 3050 |  |  | Event log ID (alarm code) 0 – 255
Alarm.LogDate | 3051 | DATE_DOS |  | Date of actual indexed event log
Alarm.LogTime | 3052 | TIME_DOS |  | Time of actual indexed event log
Alarm.LogT1 | 3053 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT3 | 3054 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT4 | 3055 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT5 | 3056 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT6 | 3057 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT7 | 3058 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT8 | 3059 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT9 | 3060 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT10 | 3061 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT11 | 3062 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT12 | 3063 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT13 | 3064 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT14 | 3065 |  | °C | Log item temperatures | measure_temperature
Alarm.LogT15 | 3066 |  | °C | Log item temperatures | measure_temperature
Alarm.LogDI_1_8i | 3067 |  |  | Log item digital input 1-8: bit 0 = input 1
Alarm.LogDI_9_16 | 3068 |  |  | Log item digital input 9-16: bit 0 = input 9
Alarm.LogDO_1_8 | 3069 |  |  | Log item digital output 1-8: bit 0 = output 1
Alarm.LogDO_9_16 | 3070 |  |  | Log item digital output 9-16: bit 0 = output 9
Alarm.LogAO_1 | 3071 |  | % | Log item analoge output 1 0 - 100
Alarm.LogAO_2 | 3072 |  | % | Log item analoge output 2
Alarm.LogAO_3 | 3073 |  | % | Log item analoge output 3 0 – 100
Alarm.LogAO_4 | 3074 |  | % | Log item analoge output 4 0 - 100
Alarm.LogCtrState | 3075 |  |  | Operation states for Control module 0: OFF
AirQual.RH_Avg | 3100 | 100 | % | Humidity average value. Range: 0..100.00 | measure_humidity
Opt9_1.BoardId | 3101 |  |  | If expansion I/O board is present the value must be 12.
AirFlow.VentState | 3102 |  |  | Ventilation state 0: OFF | thermostat_mode

## HoldingRegisters
Name | Address | Scale | Unit | Description | Min | Max | capability | Select
Bus.Address | 50 |  |  | Protocol node address (default = 30) | 0 | 255
Output.AirFlap | 100 |  |  | Air flap
Output.SmokeFlap | 101 |  |  | Smoke flap
Output.BypassOpen | 102 |  |  | Bypass flap open
Output.BypassClose | 103 |  |  | Bypass flap close
Output.AirCircPump | 104 |  |  | Air heat circulation pump
Output.AirHeatAllow | 105 |  |  | Air heating selected
Output.AirHeat_1 | 106 |  |  | Air heater relay 1
Output.AirHeat_2 | 107 |  |  | Air heater relay 2
Output.AirHeat_3 | 108 |  |  | Air heater relay 3
Output.Compressor | 109 |  |  | Compressor
Output.Compressor_2 | 110 |  |  | Compressor 2
Output.4WayCool | 111 |  |  | 4-way valve
Output.HotgasHeat | 112 |  |  | Hotgas valve - heat
Output.HotgasCool | 113 |  |  | Hotgas valve - cool
Output.CondOpen | 114 |  |  | Air condenser active
Output.CondClose | 115 |  |  | Air condenser inactive
Output.WaterHeat | 116 |  |  | Hot water heater
Output.3WayValve | 117 |  |  | Hot water 3-way valve
Output.CenCircPump | 118 |  |  | EK circulation pump
Output.CenHeat_1 | 119 |  |  | EK heater relays 1
Output.CenHeat_2 | 120 |  |  | EK heater relays 2
Output.CenHeat_3 | 121 |  |  | EK heater relays 3
Output.CenHeatExt | 122 |  |  | External radiator heat
Output.UserFunc | 123 |  |  | User function active
Output.UserFunc_2 | 124 |  |  | User function active 2
Output.Defrosting | 125 |  |  | Defrost function active
Output.AlarmRelay | 126 |  |  | Alarm relay state
Output.PreHeat | 127 |  |  | Preheater or earth tube activation
Output.ExhaustSpeed | 200 | 100 | % | Exhaust fan speed | 0 | 100
Output.InletSpeed | 201 | 100 | % | Inlet fan speed | 0 | 100
Output.AirHeatCap | 202 | 100 | % | Air heater capacity | 0 | 100
Output.CenHeatCap | 203 | 100 | % | Central heater capacity | 0 | 100
Output.CprCap | 204 | 100 | % | Compresor capacity | 0 | 100
Output.PreHeatCap | 205 | 100 | % | Preheater capacity or earth tube air intake fan speed | 0 | 100
Time.Second | 300 |  | ss | Second | 0 | 59
Time.Minute | 301 |  | nn | Minute | 0 | 59
Time.Hour | 302 |  | hh | Hour | 0 | 23
Time.Day | 303 |  | dd | Day | 1 | 31
Time.Month | 304 |  | mm | Month | 1 | 12
Time.Year | 305 |  | yyyy | Year | 2024 | 2099
Alarm.Reset | 400 |  |  | Clear one specific alarm code or all 0 : No command, 1..99 : (reserved internal commands) 101..199 : Clear alarm display code 1..99 255 : Clear all alarms | 0 | 255
Program.Select | 500 |  |  | Week program nb. select | 0 | 4 |  | ["None","Program 1", "Program 2", "Program 3", "Erase"]
Program.UserFuncAct | 600 |  |  | User function active (See “UserFuncSet”) | 0 | 6 |  | ["None","Exend","Inlet","Exhaust","External heater offset","Ventilate","Cooker Hood"]
Program.UserFuncSet | 601 |  |  | User function select | 0 | 6 |  | ["None","Exend","Inlet","Exhaust","External heater offset","Ventilate","Cooker Hood"]
Program.UserTimeSet | 602 |  | Min | User function period
Program.UserVentSet | 603 |  | Step | User function ventilation step select 0 : Off | 0 | 4 |  | ["OFF","1","2","3","4"]
Program.UserTempSet | 604 |  | °C | User function temperature (Extend function only)
Program.UserOffsSet | 605 |  | °C | User function temperature offset (Offset function only)
Program.User2FuncAct | 610 |  |  | User function active (See “UserFuncSet”) | 0 | 6 |  | ["None","Exend","Inlet","Exhaust","External heater offset","Ventilate","Cooker Hood"]
Program.User2FuncSet | 611 |  |  | User2function select | 0 | 6 |  | ["None","Exend","Inlet","Exhaust","External heater offset","Ventilate","Cooker Hood"]
Program.User2TimeSet | 612 |  |  | User2 function period
Program.User2VentSet | 613 |  |  | User2 function ventilation step select 0 : Off | 0 | 4 |  | ["OFF","1","2","3","4"]
Program.User2TempSet | 614 |  |  | User2 function temperature (Extend function only)
Program.User2OffsSet | 615 |  |  | User2 function temperature offset (Offset function only)
Log.Interval | 700 |  | Min | Periodic data log interval select 0: Off 1..120: Time between periodic loggings | 0 | 120
Control.Type | 1000 |  |  | Machine type select (factory setting)
Control.RunSet | 1001 |  | OnOff | User on / off select (equal to ON/OFF keys)
Control.ModeSet | 1002 |  |  | User operation mode select | 0 | 4 |  | ["Off","Heat","Cool","Auto","Service (readonly)"]
Control.VentSet | 1003 |  | Step | User ventilation step select 0 : Off | 0 | 4 |  | ["Off","1","2","3","4"]
Control.TempSet | 1004 | 100 | °C | User temperature setpoint
Control.ServiceMode | 1005 |  |  | Service mode select |  |  |  | ["Off","Defrost","Flaps","Inlet","Exhaust","Compressor","Heating","Hot water","Central heat"]
Control.ServicePct | 1006 | 100 | % | Service mode capacity setpoint
Control.Preset | 1007 |  |  | Request preset to default settings |  |  |  | ["Ready","Standard (to factory defaults)","Backup (to user file)","Restore (from user file)"]
AirFlow.AirExchMode | 1100 |  |  | Air exchange mode
AirFlow.CoolVent | 1101 |  | Step | Cooling high ventilation step
AirFlow.TestSelect | 1102 |  |  | Select a day for weekly air damper position self-test The test runs at 10 in the morning on the selected day Once enabled, the function cannot be deactivated
AirFlow.LastTestDay | 1103 |  |  | Date of last air damper position test Bit word packed in DOS date format (see IR 402 format)
AirFlow.TestState | 1104 |  |  | Actual air damper position test state 0: Off
AirFlow.FiltAlmType | 1105 |  |  | Air filter monitoring alarm type and period select 0: Pressure guard (input)
AirTemp.CoolSet | 1200 |  |  | Cooling temperature setpoint select
AirTemp.TempMinSum | 1201 | 100 | °C | Inlet temp. min. summer
AirTemp.TempMinWin | 1202 | 100 | °C | Inlet temp. min. winter
AirTemp.TempMaxSum | 1203 | 100 | °C | Inlet temp. max. summer
AirTemp.TempMaxWin | 1204 | 100 | °C | Inlet temp. max. winter
AirTemp.TempSummer | 1205 | 100 | °C | Summer/winter limit
AirTemp.NightDayLim | 1206 | 100 | °C | Outdoor day temperature for night cooling activation [0:Off, 20..40]
AirTemp.NightSet | 1207 | 100 | °C | Free energy night cooling room setpoint [10..30]
AirTemp.SensorSelect | 1208 |  |  | Control temperature sensor select 0: User panel
AirTemp.HeatSelect | 1209 | 1 |  | Valg af varmekilde: 0=No heating active, 1=Heatpump only, 2=HP+afterheat, 3=Afterheat only,
Compressor.CondTempMin | 1500 | 100 |  | Low temperaturcurve.
Compressor.CondTempMax | 1501 | 100 |  | High temperaturcurve
AirTemp.TempMinCpr | 1502 | 100 |  | Low temperature compressor start
AirTemp.CprRestart | 1503 | 60 |  | Compressor stop time
HotWater.TempSet_T11 | 1700 | 100 | °C | Top temperature setpoint (electric)
HotWater.TempSet_T12 | 1701 | 100 | °C | Bottom temperature setpoint (compressor)
HotWater.Priority | 1702 | 1 |  | Priority: 0=Water, 1=Inlet
HotWater.TempCprMax | 1703 | 100 |  | Scald protection Temperature
HotWater.HeatType | 1704 | 1 |  | Use of electricity supplement:
0=OFF, 1=El
HotWater.LegioType | 1705 | 1 |  | Day for legionella:
0=OFF,1=Mandag,1=tirsdag, ..., 7=søndag
HotWater.TempPri | 1706 | 1 | °C | Bypass offset: 0=Off, 1..30°C | 0 | 30
CentralHeat.HeatExtern | 1800 | 100 | °C | External heating offset from room temperature setpoint
CentralHeat.HeatSelect | 1801 | 1 |  | 0=Only Pump motion and freze secure, 1=Always central heating,
CentralHeat.SupplyMin | 1802 | 100 | °C | Min supply temperature
CentralHeat.SupplyMax | 1803 | 100 | °C | Max supply temperature
CentralHeat.SupplyOffset | 1804 | 100 | °C | Outdoor temperature compensation
CentralHeat.CurveSelect | 1805 | 1 |  | Temp. compensation curve: 1-10
CentralHeat.CircPumpMode | 1806 | 1 |  | 0=Only when heating is active, 1=Continuous operation
CentralHeat.HeatType | 1807 | 1 |  | 0=OFF,
CentralHeat.RegTime | 1808 | 1 | Sec | PID regulations time: 0=2sec, 1-25(sec)
AirQual.RH_VentLo | 1910 |  | Step | Humidity low winter step select
AirQual.RH_VentHi | 1911 |  | Step | Humidity high step select
AirQual.RH_LimLo | 1912 | 100 | % | Humidity limit for low ventilation
AirQual.RH_TimeOut | 1913 |  | min | Humidity max. time on high ventilation
AirQual.CO2_VentHi | 1920 |  | Step | CO2 high step select
AirQual.CO2_LimLo | 1921 |  | ppm | CO2 limit for normal ventilation
AirQual.CO2_LimHi | 1922 |  | ppm | CO2 limit for high ventilation
User. UserMenuOpen | 2002 |  |  | Menu is open:
User.Language | 2003 | 1 |  | HMI language: 0=English 1=German 2=French 3=Swedish 4=Danish 5=Norwegian 6=Finnish 7=Czech 8=Polish 9=Italian | 0 | 9 |  | ["English","German","French","Swedish","Danish","Norwegian","Finish","Czech","Polish","Italian"]
PreHeat.Block | 2100 |  |  | COMFORT(n) only
DPT.DoCalibrate | 2200 |  | 0.1 | Calibrate DPT.
1: Start calibration
CentralHeat.HeatExtern | 4000 | 100 | °C | Regulation deadband external room heating | -5 | 5
AirFlow.CoolVent | 4001 |  |  | High fan speed at high indoor temp (cooling demand) Level OFF, 2-4
AirFlow.WinterTemp | 4002 | 1 | °C | Low outdoor temperature | -20 | 10
-20°C - 10°C
AirFlow.WinerVent | 4003 |  |  | Fan speed at low outdoor temperature 0: OFF |  |  |  | ["OFF","1","2","3"]
AirFlow.TestSelect | 4004 |  |  | Day for automatic test 0: OFF |  |  |  | ["OFF","Monday","Tuesday","Wednesday","Thursday","Friday","Saturday","Sunday"]
1: Mo
2: Tu
3: We
4: Th
5: Fr
6: Sa
7: Su
AirHeat.Type | 4005 |  |  | After heating type
0: No additional heat 1: Electrical
2: Electric on binary relays 3: Water
AirHeat.Delay | 4006 | 1 | Min | Delay timer for after-heat activation 0-60 min.
AirTemp.TempMinSum | 4007 | 100 | °C | Summer minimum supply air temperature MinSum: 5.00-14.00
AirTemp.TempMaxSum | 4008 | 100 | °C | Summer maximum supply air temperature MaxSum: 5.00-25.00
AirTemp.TempMinWin | 4009 | 100 | °C | Winter minimum supply air temperature MinWin: 5.00-16.00
AirTemp.TempMaxWin | 4010 | 100 | °C | Winter maximum supply air temperature MaxWin: 5.00-35.00
AirTemp.RoomNZ | 4011 | 100 |  | Room temperature regulation deadband
0.20 – 10.00
AirTemp.TempRoomLow | 4012 | 100 | °C | Low room temperature for stepwise reduced ventilation 0: OFF | 1 | 20
AirHeat.SelectSet | 4013 |  |  | After heating activation: |  |  |  | ["Off","On (No effect if Airheat is off)"]
0: Off
1: On (No effect is AirHeat.Type (H4005) is 0.)
AirFlow.InletMin | 4015 | 1 |  | Min. inlet: 0-2 | 0 | 2
AirFlow.ExhaustMin | 4016 | 1 |  | Min exhaust: 1-2 | 1 | 2
AirFlow.ExhaustMax | 4017 | 1 |  | Max exhaust:
AirFlow.StartDelay | 4018 | 60 |  | Start delay
AirBypass.WalkingTime | 4019 | 1 | Sec | Damper walkin time: 60-900 sec.
Defrost.Fans | 4020 |  |  | Frost protection or de-icing - Ventilation level 0: OFF |  |  |  | ["OFF","USER","LOW"]
Defrost.Bypass | 4021 |  |  | Frost protection or de-icing - Bypass position 0: OFF |  |  |  | ["OFF","ON"]
Defrost.BlockMinutes | 4022 | 1 | Min | Frost protection or de-icing - Time between activations 15 - 720
Defrost.TempStart | 4023 | 100 | °C | Frost protection or de-icing - Start criteria | -10 | 0
Defrost.TempStop | 4024 | 100 | °C | Frost protection or de-icing - Stop criteria 2.00°C – 12.00°C
Defrost.DurMaxCpr | 4025 | 1 | Min | Frost protection or de-icing - Max duration compressor 2 – 60 | 2 | 60
Defrost.DurMaxExh | 4026 | 1 | Min | Frost protection or de-icing - Max duration exchanger 5 – 60 | 5 | 60
Defrost.T6MinRunSec | 4027 | 1 | Sec | T6 min defrost time: 10-120sec. | 10 | 120
Program.EditIndex | 4030 |  |  | Week program - Index: 0-41 (7 days multiply by 6 functions each day) | 0 | 41
Program.EditPeriod | 4031 |  |  | Week program |  |  |  | ["Monday","Tuesday","Wednesday","Thursday","Friday","Saturday","Sunday"]
Program.EditPeriodNx | 4032 |  |  | Week program |  |  |  | ["Monday","Tuesday","Wednesday","Thursday","Friday","Saturday","Sunday"]
Program.EditFunc | 4033 |  |  | Week program Day function 0-5. | 0 | 5
Program.EditTimeStar | 4034 |  |  | Week program start time (1215 = 12:15) | 0 | 2345
Program.EditVent | 4035 |  |  | Week program Fan settings: 0-4 0=Off, |  |  |  | ["OFF","1","2","3","4"]
Program.EditTemp | 4036 | 1 | °C | Week program Temperature: 5°C - 50°C
Control.RestartMode | 4040 |  |  | External fire alarm auto reset 0: OFF | 0 | 3 |  | ["OFF", "HPLP", "CONTINUE", "SELF_CLEAR"]
Control.PowerSave | 4041 |  |  | Enable power saving features 0: OFF |  |  |  | ["OFF","ON"]
Alarm.LogIndex | 4050 |  |  | Alarm log index 0 - 15
AirFlow.InletScale | 4098 |  | % | Scaling of inlet fan control voltage for max. air volume Range: 50..100 | 50 | 100
AirFlow.ExhaustScale | 4099 |  | % | Scaling of exhaust fan control voltage for max. air volume Range: 50..100 | 50 | 100
AirFlow.InletSpd_1 | 4100 |  |  | Inlet step 1 speed setup Range: 20..100 | 20 | 100
AirFlow.InletSpd_2 | 4101 |  |  | Inlet step 2 speed setup Range: 20..100 | 20 | 100
AirFlow.InletSpd_3 | 4102 |  |  | Inlet step 3 speed setup Range: 20..100 | 20 | 100
AirFlow.InletSpd_4 | 4103 |  |  | Inlet step 4 speed setup Range: 20..100 | 20 | 100
AirFlow.ExhaustSpd_1 | 4104 |  |  | Exhaust step 1 speed setup Range: 20..100 | 20 | 100
AirFlow.ExhaustSpd_2 | 4105 |  |  | Exhaust step 2 speed setup Range: 20..100 | 20 | 100
AirFlow.ExhaustSpd_3 | 4106 |  |  | Exhaust step 3 speed setup Range: 20..100 | 20 | 100
AirFlow.ExhaustSpd_4 | 4107 |  |  | Exhaust step 4 speed setup Range: 20..100 | 20 | 100
AirQual.Type | 4108 |  |  | Enable Indoor Air Quality (IAQ) control function Range: 0..2 | 0 | 2
Control.AnaOutType | 4109 |  |  | Heater output signal type (if not air channel type) Range: 0..4 | 0 | 4
AirTemp.RoomResponse | 4110 |  |  | Room temperature controller response type Select predefined or user adjustable parameters Range: 0..3 | 0 | 3
PreHeat.Defrost | 4111 |  |  | Nordic: Select anti frost also during evap. defrost COMFORT: Select T8 preheater allowance on R5 Range: 0..1 | 0 | 1
PreHeat.TempSet | 4112 |  |  | T4 start criteria when temperature controlled exchanger defrosting is selected (without no-frost) Range: 0..5 | 0 | 5

## Utils
on | yes | open | true
off | no | closed | false

## Classes
Name | ID | Description | Allows Virtual
Amplifier | amplifier | Use this device class for audio amplifier devices. | no
Blinds | blinds | Use this device class for blinds, both horizontal and vertical. | no
Button | button | Use this device class for buttons, such as a remote. | no
Camera | camera | Security camera | no
Coffee machine | coffeemachine | Use this device class for coffee machines. | no
Curtains | curtain | Use this device class for curtains. | no
Doorbell | doorbell | Use this device class for doorbells, usually together with the `button` capability. | no
Fan | fan | Use this device class for fans that cool your home. | no
Garage door | garagedoor | Use this device class for garage doors, usually together with the `garagedoor_closed` capability. | no
Heater | heater | Use this device class for heaters, that warm your home. | no
Home Security | homealarm | Use this device class for home alarm systems. | no
Kettle | kettle | Use this device class for kettle devices, that can heat water. | no
Light | light | Use this device class for lights, usually together with the `onoff`, `dim` and `light_*` capabilities. | no
Lock | lock | Use this device class for lock devices, usually together with the `locked` and `lock_mode` capabilities. | no
Other | other | Use this device class for devices that do not fit any other device class. | no
Remote | remote | Use this device class for (TV/Sunblind/Keyfob etc.) remotes. | no
Sensor | sensor | Use this device class for sensors, e.g. a contact or motion sensor. | no
Wall Plug | socket | Use this device class for sockets (built-in or plug-in socket switches). When adding the `choose_slave` pair template, the user is presented a `What's plugged in?` question. | yes
Speaker | speaker | Use this device class for devices that can play music, usually together with the `speaker_*` capabilities. | no
Solar Panel | solarpanel | Use this device class for solar panels. | no
Sunshade | sunshade | Use this device class for sunshades (window coverings against the sun). | no
Thermostat | thermostat | Use this device class for thermostats, either for the entire home or radiator-mounted, usually together with the `measure_temperature`, `target_temperature` and `thermostat_mode` capabilities. | no
TV | tv | Use this device class for TVs. | no
Vacuum Cleaner | vacuumcleaner | Use this device class for vacuum cleaners, usually together with the `vacuumcleaner_state` capability. | no
Window Coverings | windowcoverings | Use this device class for window coverings, when the `curtains`, `blinds` or `sunshade` device class doesn't apply. | yes
yes
no

## Capabilities
Name | ID | Type | Getable | Setable | Insights | Quick Action | Flow | UI Component
Turned on | onoff | boolean | true | false |  |  |  | toggle
Dim level | dim | number | true | false |  |  |  | slider
Hue | light_hue | number | true | false |  |  |  | color
Color saturation | light_saturation | number | true | false |  |  |  | color
Color temperature | light_temperature | number | true | false |  |  |  | color
Light mode | light_mode | enum | true | false |  |  |  | color
Vacuum cleaner state | vacuumcleaner_state | enum | true | false |  |  |  | picker
Thermostat mode | thermostat_mode | enum | true | false |  |  |  | picker
Target temperature | target_temperature | number | true | false |  |  |  | thermostat
Temperature | measure_temperature | number | true | false |  |  |  | sensor
CO | measure_co | number | true | false |  |  |  | sensor
CO2 | measure_co2 | number | true | false |  |  |  | sensor
PM2.5 | measure_pm25 | number | true | false |  |  |  | sensor
Humidity | measure_humidity | number | true | false |  |  |  | sensor
Pressure | measure_pressure | number | true | false |  |  |  | sensor
Noise | measure_noise | number | true | false |  |  |  | sensor
Rain | measure_rain | number | true | false |  |  |  | sensor
Wind strength | measure_wind_strength | number | true | false |  |  |  | sensor
Wind angle | measure_wind_angle | number | true | false |  |  |  | sensor
Gust strength | measure_gust_strength | number | true | false |  |  |  | sensor
Gust angle | measure_gust_angle | number | true | false |  |  |  | sensor
Battery | measure_battery | number | true | false |  |  |  | battery
Power | measure_power | number | true | false |  |  |  | sensor
Voltage | measure_voltage | number | true | false |  |  |  | sensor
Current | measure_current | number | true | false |  |  |  | sensor
Luminance | measure_luminance | number | true | false |  |  |  | sensor
Ultraviolet | measure_ultraviolet | number | true | false |  |  |  | sensor
Water flow | measure_water | number | true | false |  |  |  | sensor
Generic alarm | alarm_generic | boolean | true | false |  |  |  | sensor
Motion alarm | alarm_motion | boolean | true | false |  |  |  | sensor
Contact alarm | alarm_contact | boolean | true | false |  |  |  | sensor
CO alarm | alarm_co | boolean | true | false |  |  |  | sensor
CO2 alarm | alarm_co2 | boolean | true | false |  |  |  | sensor
PM2.5 alarm | alarm_pm25 | boolean | true | false |  |  |  | sensor
Tamper alarm | alarm_tamper | boolean | true | false |  |  |  | sensor
Smoke alarm | alarm_smoke | boolean | true | false |  |  |  | sensor
Fire alarm | alarm_fire | boolean | true | false |  |  |  | sensor
Heat alarm | alarm_heat | boolean | true | false |  |  |  | sensor
Water alarm | alarm_water | boolean | true | false |  |  |  | sensor
Battery alarm | alarm_battery | boolean | true | false |  |  |  | battery
Night alarm | alarm_night | boolean | true | false |  |  |  | sensor
Energy | meter_power | number | true | false |  |  |  | sensor
Water meter | meter_water | number | true | false |  |  |  | sensor
Gas meter | meter_gas | number | true | false |  |  |  | sensor
Rain meter | meter_rain | number | true | false |  |  |  | sensor
Home alarm state | homealarm_state | enum | true | false |  |  |  | picker
Set volume | volume_set | number | true | false |  |  |  | slider
Volume up | volume_up | boolean | true | false |  |  |  | button
Volume down | volume_down | boolean | true | false |  |  |  | button
Volume muted | volume_mute | boolean | true | false |  |  |  | button
Channel up | channel_up | boolean | true | false |  |  |  | button
Channel down | channel_down | boolean | true | false |  |  |  | button
Locked | locked | boolean | true | false |  |  |  | toggle
Lock mode | lock_mode | enum | true | false |  |  |  | picker
Closed | garagedoor_closed | boolean | true | false |  |  |  | toggle
Window coverings state | windowcoverings_state | enum | true | false |  |  |  | ternary
Window coverings tilt up | windowcoverings_tilt_up | boolean | true | false |  |  |  | button
Window coverings tilt down | windowcoverings_tilt_down | boolean | true | false |  |  |  | button
Window coverings tilt set | windowcoverings_tilt_set | number | true | false |  |  |  | slider
Closed | windowcoverings_closed | boolean | true | false |  |  |  | toggle
Position | windowcoverings_set | number | true | false |  |  |  | slider
Button | button | boolean | true | false |  |  |  | button
Playing | speaker_playing | boolean | true | false |  |  |  | media
Next | speaker_next | boolean | true | false |  |  |  | media
Previous | speaker_prev | boolean | true | false |  |  |  | media
Shuffle | speaker_shuffle | boolean | true | false |  |  |  | media
Repeat | speaker_repeat | enum | true | false |  |  |  | media
Artist | speaker_artist | string | true | false |  |  |  | media
Album | speaker_album | string | true | false |  |  |  | media
Track | speaker_track | string | true | false |  |  |  | media
Duration | speaker_duration | number | true | false |  |  |  | media
Position | speaker_position | number | true | false |  |  |  | media

## HoldingOverview
Name | Address | RegCount | Description
Bus | 50 | 1 | Bus adressing
Output1 | 100 | 28 | Output registers - 1
Output2 | 200 | 6 | Output registers - 2
Time | 300 | 6 | Clock and calendar
Alarm | 400 | 1 | Alarm and message handling
Week program | 500 | 1 | Calendar based programming
User functions | 600 | 6 | User input function selection
User 2 functions | 610 | 6 | User 2 input function selection
Data log | 700 | 1 | Data, alarm and event logging
Control | 1000 | 8 | System control and status
AirFlow | 1100 | 6 | Ventilation control
AirTemp | 1200 | 10 | Room temperature control
Compressor | 1500 | 4 | Compressor operation control
HotWater | 1700 | 7 | Hot water control
CentHeat | 1800 | 9 | Central heating control (EK)
AirQual | 1900 | 23 | Air quality control (RH, CO2)
User panel | 2002 | 2 | Display and keyboard
PreHeat | 2100 | 1 | Intake air preheat / earth tube
DPT | 2200 | 1 | Difference pressure transducer
Defrost | 4000 | 28 | Defrost
Program | 4030 | 7 | Weekly program
Control | 4040 | 2 | Control
Alarm | 4050 | 1 | Alarm
AirFlow | 4098 | 10 | Airflow
AirQuality | 4108